## PPG
system | equipment number | material constructioons | surface temperature （℃） | with/without insulation |  | corrosion grade ISO 12944 | Average RH | Avg. Dew Point Temperature | Required Durability (year) | Coating Type |  | Coating Components Ratio | Thinner Ratio | Recommended Mixing Methods/Time (minute) |  | Required Surface Roughness (um) | Required Surface Cleanliness | Required Surface Salts Contents | Recommended Surface Preparation Methods |  | Recommended Painting Methods |  | Layers |  | Required Total DFT (um) | Required Curing Time (hours) | Remark
|  |  |  | Y/N | Materials | [8 empty] | Method | Time |  |  |  | Flat Area | Edge Area | Flat Area | Edge Area | Layers | Time Interval
管廊钢结构/平台/护栏/支架 |  | 碳钢 | 常温 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
镀锌管线、镀锌件表面 |  | 镀锌 | 25 | N |  | C5-I/C5M | 80 | 20.9 | >10 years | Prime | Sigmacover 280 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 |  | 表面清洁 | 120mg/m2(NaCl)/144mg/m2(NaCl)(PPG最大值） | 表面拉毛 | 表面拉毛 | 推荐高压无气喷涂（可以有气喷涂、刷涂、滚涂） | 推荐高压无气喷涂（可以有气喷涂、刷涂、滚涂） | 1 | 8H | 50 | 8H
[10 empty] | Intermediate |  |  | 15% | 搅拌器
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 推荐高压无气喷涂（可以有气喷涂、刷涂、滚涂） | 推荐高压无气喷涂（可以有气喷涂、刷涂、滚涂） | 1 | 6H | 80 | 6H
[10 empty] | Thinner | 91-92/ 21-06 |  | 15% | 搅拌器
非保温储罐 |  | 碳钢 | 常温 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
保温储罐 |  | 碳钢 | 25 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92 |  | 15% | 搅拌器
保温储罐 |  | 碳钢 | 60 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92
保温储罐 |  | 碳钢 | 90 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92
保温储罐 |  | 碳钢 | 100 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92
非保温管道 |  | 碳钢 | 常温 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
保温管道 |  | 碳钢 | 25 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92
保温管道 |  | 碳钢 | 60 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92
保温管道 |  | 碳钢 | 90 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92
保温管道 |  | 碳钢 | 100 | Y | 硅酸铝 | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
Intermediate
[10 empty] | Top | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 150 | 8H
[10 empty] | Thinner | 91-92
电机 |  | 碳钢 | 常温 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
输油臂/泵体 |  | 碳钢 | 常温 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
输油臂/泵体 |  | 碳钢 | 25 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
输油臂/泵体 |  | 碳钢 | 60 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
输油臂/泵体 |  | 碳钢 | 90 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06
输油臂/泵体 |  | 碳钢 | 100 | N |  | C5 | 77 | 22.4 | >15 years | Prime | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | 40-70(喷砂） | Sa2.5 or ST3 | 144mg/m2(NaCl) | 喷砂 | 喷砂 | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Intermediate | Sigmacover 620 | 基料：固化剂=80：20 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先喷涂/后预涂 | 1 | 8H | 120 | 8H
[10 empty] | Top | Sigmadur 550 | 基料：固化剂=88：12 | 15% | 搅拌器 | 3~5 | [5 empty] | 高压无气喷涂 | 先预涂/后喷涂 | 1 | 6H | 60 | 6H
[10 empty] | Thinner | 91-92/21-06

## JOTUN 佐敦
system | equipment number | material constructioons | surface temperature （℃） | with/without insulation |  | corrosion grade ISO 12944 | Average RH, % | Avg. Dew Point Temperature, ℃ | Required Durability (year) | Coating Type |  | Thinner | Coating Components Ratio | Thinner Ratio | Recommended Mixing Methods/Time (minute) |  | Recommended Surface Preparation Methods |  | Required Surface Cleanliness |  | Required Surface Roughness (um) |  | Required Surface Salts Contents | Recommended Painting Methods |  | Layers |  |  | Required Total DFT (um) | Required Curing Time (hours) | Remark
|  |  |  | Y/N | Materials | [9 empty] | Method | Time | Flat Area | Edge Area | Flat Area | Edge Area | Flat Area | Edge Area |  | Flat Area | Edge Area | Layers, Airless spray | Layers, Brush / Roller | Dry to ovecoat, min, 23℃
管廊钢结构/平台/护栏/支架 |  | 碳钢 | 常温 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
非保温储罐 |  | 碳钢 | 常温 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
保温储罐 |  | 碳钢 | 25 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
保温储罐 |  | 碳钢 | 60 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
保温储罐 |  | 碳钢 | 90 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
保温储罐 |  | 碳钢 | 100 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
非保温管道 |  | 碳钢 | 常温 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
保温管道 |  | 碳钢 | 25 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
保温管道 |  | 碳钢 | 60 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
保温管道 |  | 碳钢 | 90 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
保温管道 |  | 碳钢 | 100 | Y | 硅酸铝 | C5 | 75 | 17 | >15 years | Prime | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
Intermediate
[10 empty] | Top | Penguard EXA II | Jotun Thinner No.17 | 3:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 4h | 100 | Depend on temperature, see TDS
电机 |  | 碳钢 | 常温 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
输油臂/泵体 |  | 碳钢 | 常温 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
输油臂/泵体 |  | 碳钢 | 25 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
输油臂/泵体 |  | 碳钢 | 60 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
输油臂/泵体 |  | 碳钢 | 90 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS
输油臂/泵体 |  | 碳钢 | 100 | N |  | C5 | 75 | 17 | >15 years | Prime | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | Wet blasting | Hand or power-tool cleaning | Sa2.5 | St2 or St3 | 30-85um | N/A | 100mg/m2 | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Intermediate | Jotamastic 70 | Jotun Thinner No.17 | 5:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 2-3 | 7h | 120 | Depend on temperature, see TDS
[10 empty] | Top | Futura Classic | Jotun Thinner No.10 | 9:1 | 5% - 10% | Mechanical stirring | 5 min (reference) | [7 empty] | Airless spray; Brush / Roller | Airless spray; Brush / Roller | 1 | 1-2 | 7h | 60 | Depend on temperature, see TDS

## HEMPEL 海虹老人
system | equipment number | material constructioons | surface temperature （℃） | with/without insulation |  | corrosion grade ISO 12944 | Average RH | Avg. Dew Point Temperature | Required Durability (year) | Coating Type |  | Coating Components Ratio | Thinner Ratio | Recommended Mixing Methods/Time (minute) |  | Required Surface Roughness (um) | Required Surface Cleanliness | Required Surface Salts Contents | Recommended Surface Preparation Methods |  | Recommended Painting Methods |  | Layers |  | Required Total DFT (um) | Required Curing Time (hours) | Remark
|  |  |  | Y/N | Materials | [8 empty] | Method | Time |  |  |  | Flat Area | Edge Area | Flat Area | Edge Area | Layers | Time Interval
管廊钢结构/平台/护栏/支架 |  | 碳钢 | 常温 | N |  | C5-I | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃ | 表面处理方式说明：
[10 empty] | Intermediate | [16 empty] | 优先选用湿喷砂作业，表面处理等级为Sa 2.5; 同时添加适量缓蚀剂减缓闪锈；边缘、角落等采用人工打磨；
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner
非保温储罐 |  | 碳钢 | 常温 | N |  | C5-I | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
[10 empty] | Intermediate | [16 empty] | 可以动火条件下，推荐采用干喷砂作业，表面处理等级为Sa 2.5；边缘、角落等采用人工打磨；
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner
保温储罐 |  | 碳钢 | 25 | Y | 硅酸铝 | C5-I | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃
Intermediate
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃ | 涂层道数说明：
[10 empty] | Thinner | [16 empty] | X列中数字表示选用Airless-无气喷涂方式时，推荐一道成膜厚度；
保温储罐 |  | 碳钢 | 60 | Y | 硅酸铝 | C5-I | less than 79% | less than 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃
Intermediate
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃
[10 empty] | Thinner | [16 empty] | 如无法进行喷涂作业，选用Roller/Brush，单道膜厚按照40um计，最终达到推荐干膜膜厚；
保温储罐 |  | 碳钢 | 90 | Y | 硅酸铝 | C5-I | less than 79% | less than 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃
Intermediate
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃
Thinner
保温储罐 |  | 碳钢 | 100 | Y | 硅酸铝 | C5-I | less than 79% | less than 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃ | 重涂间隔说明：
[10 empty] | Intermediate | [16 empty] | 如采用无气喷涂方式，底漆与面漆，20°C温度下最大重涂间隔为10天，超出重涂间隔时间需要对表面进行拉毛；
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃
Thinner
非保温管道 |  | 碳钢 | 常温 | N |  | C5-I | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
Intermediate
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃ | 如采用刷涂/辊涂等方式，底漆与底漆重涂间隔可以适当延长；详情参考厂商建议
Thinner
保温管道 |  | 碳钢 | 25 | Y | 硅酸铝 | C5-I | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃
[10 empty] | Intermediate | [16 empty] | 如采用刷涂/辊涂等方式，面漆与面漆的重涂间隔可以适当延长； 详情参考厂商建议
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃
Thinner
保温管道 |  | 碳钢 | 60 | Y | 硅酸铝 | C5-I | less than 79% | less than 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃
Intermediate
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃
Thinner
保温管道 |  | 碳钢 | 90 | Y | 硅酸铝 | C5-I | less than 79% | less than 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃
Intermediate
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃
Thinner
保温管道 |  | 碳钢 | 100 | Y | 硅酸铝 | C5-I | less than 79% | less than 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 1 | No more than 10 days | 120 | 10 days/20℃
Intermediate
[10 empty] | Top | 17720 | 3:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 | 100mg/m2 |  |  | Airless/Roller | Brush/Roller | 1 |  | 120 | 10 days/20℃
Thinner
电机 |  | 碳钢 | 常温 | N |  | C5-I | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
Intermediate
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner
输油臂/泵体 |  | 碳钢 | 常温 | N |  | C5-M | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
Intermediate
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner
输油臂/泵体 |  | 碳钢 | 25 | N |  | C5-M | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
Intermediate
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner
输油臂/泵体 |  | 碳钢 | 60 | N |  | C5-M | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
Intermediate
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner
输油臂/泵体 |  | 碳钢 | 90 | N |  | C5-M | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
Intermediate
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner
输油臂/泵体 |  | 碳钢 | 100 | N |  | C5-M | 79% | 25℃ | >15 years | Prime | 17720 | 3:1 | 5% | Mechanical stir | 2 hours | 25-60 | 湿喷砂+打磨（不动火） 干喷砂+打磨 （动火） | 100mg/m2 | Sa2.5 (首选湿喷砂) | St2 (无法进行喷砂区域) | Airless/Roller | Brush/Roller | 2 | No more than 10 days | 240 | 10 days/20℃
Intermediate
[10 empty] | Top | 55610 | 7:1 | 5% | Mechanical stir | 2 hours |  | 如超出最大重涂间隔，拉毛处理 |  |  |  | Airless/Roller | Brush/Roller | 1 |  | 60 | 7 days/20℃
Thinner